# Smart Grid Monitoring System

Specification Document — Energy Domain

Version 1.0 | Classification: Internal

# 1. Scope

This document specifies the requirements for a Smart Grid Monitoring System (SGMS) designed to monitor electrical grid parameters in real-time, detect anomalies, and generate automated alerts for grid operators.

# 2. Functional Requirements

## 2.1 Data Acquisition

REQ-001: The system shall acquire voltage, current, and power measurements from each monitored node at a minimum sampling rate of 1 kHz.

REQ-002: The system shall support simultaneous monitoring of up to 500 grid nodes.

REQ-003: The system shall store measurement data for a minimum retention period of 365 days.

## 2.2 Anomaly Detection

REQ-004: The system shall detect voltage sags exceeding 10% of nominal voltage within 100 ms of occurrence.

REQ-005: The system shall detect frequency deviations greater than 0.5 Hz from the nominal 50 Hz grid frequency.

REQ-006: The system shall detect power factor values below 0.85 and generate a warning alert.

## 2.3 Alerting

REQ-007: The system shall generate real-time alerts via email and SMS within 5 seconds of anomaly detection.

REQ-008: The system shall classify alerts into three severity levels: Critical, Warning, and Informational.

# 3. Performance Requirements

REQ-009: The system data processing latency shall not exceed 50 ms from measurement to dashboard display.

REQ-010: The system shall maintain 99.95% uptime availability over any 30-day period.

# 4. Interface Requirements

REQ-011: The system shall provide a REST API for third-party integration with response time under 200 ms.

REQ-012: The system shall support Modbus TCP/IP and IEC 61850 communication protocols for sensor data acquisition.

# 5. Security Requirements

REQ-013: All data transmission between sensors and the central system shall be encrypted using TLS 1.3.

REQ-014: The system shall enforce role-based access control with a minimum of three roles: Operator, Engineer, and Administrator.